REQUIRED MUST-RUN GENERATION

TUCSON CONTROL AREA

FOR THE YEARS 2005, 2008, 2012

PREPARED FOR THE ARIZONA CORPORATION COMMISSION

Mary Ann Tilford

Transmission System Planning

Tucson Electric Power

December 4, 2003

TEP OPERATING CRITERIA AND OUTAGE RESPONSE

The TEP control area has historically been voltage stability constrained. Local Var-responsive steam units and combustion turbines can be committed in the Tucson load area to supply reactive support and to lower imports as necessary. In addition, TEP has an automated deterministic remedial action scheme that responds to selected single and double contingencies with pre-determined switching of reactive devices and / or direct load tripping.  This remedial action scheme was designed assuming a fast collapse, and all actions take place in a maximum of .7 seconds after breakers open.

Fifty percent of customer load is available for arming for direct tripping, and there are three fast-switched reactive devices (RADs) available for arming. The fast-switched devices are the line reactor on the South end of the Westwing-South transmission line; two 44 MVar banks of capacitors on the 13.8 tertiary of the Vail 345/138 kV T1; and a 138kV, 39.6 MVar capacitor at Northeast Substation.

For single contingencies, the most economical combination of local generation and RADs is utilized to ensure that contingencies meet WECC / NERC voltage stability and reliability criteria, and TEP’s internal voltage criterion of .98 per unit post-outage 138 kV average voltage.

RMR generation is in response to the reliability criterion defined by the Second Biennial Transmission Assessment, 2002-2011, which states “…reliability practices are founded on the principle of continuity of service for single contingency outages (N-1) of transmission lines.” It should be noted that Tucson Electric Power Co. plans and operates its system to meet the WECC / NERC Reliability Criteria for both level B (N-1) and Level C (N-2; N-1-1) contingencies, as well as the WECC Voltage Stability Criteria.

Please note that the generating units formerly referred to as Irvington units, are now referred to as Sundt units.

BASE CASE DESCRIPTIONS:

All base cases used were co-developed by APS, SRP, TEP, WAPA, and SWTC.  Planned system configuration changes for all these utilities were used to develop the various cases.

Below is a description of TEP’s portion of the respective cases:

2005:

New Facilities:

Winchester 345kV Substation (2004)

Greenlee-Copper Verde 345 kV line (2004)

Gateway 345kV substation connecting to Citizens/Unisource 115 kV system at Valencia via a 345/115 kV transformer (2005)

Two 345 kV transmission lines between TEP’s South and Gateway substations (2005)

Facility Upgrades:

Twenty-second / East Loop 138kV line upgraded from 225 MVA to 391 MVA (2004)

Twenty-second / Irvington 138kV line upgraded from 331 MVA to 444 MVA (2005)

Peak Load:

2000 MW (per official TEP forecast)

2008:

New Facilities:

Pinal-West 345 kV substation and interconnection to Westwing-South 345 kV line (2006)

Facility Upgrades:

Rillito / LaCanada 138kV line upgraded from 340 MVA to 356 MVA (2008)

North Loop / Rillito 138kV line upgraded from 287 MVA to 339 MVA (2008)

Peak Load:

2121 MW (per official TEP forecast)

2012:

New Facilities:

Tortolita – South 345 kV transmission line and associated 500/345 kV transformer at Tortolita (TBD)

Pinal West – Tortolita 500 kV line (TBD)

Facility upgrades:

Irvington / South 138kV line upgraded from 309 MVA to 394 MVA (2009)

Irvington / Vail #1 138kV line upgraded from 287 MVA to 356 MVA (2009)

Irvington / Vail #2 138kV line upgraded from 287 MVA to 356 MVA (2009)

Peak Load:

2287 MW (per official TEP forecast)

IMPORT TRANSMISSION ELEMENTS BY YEAR

Year	From		KV	To		KV	CK	30 Minute Rating

2005	Saguaro		500	Tortolita		500	1	806 MVA (xfmr)

Saguaro		500	Tortolita		500	2	806 MVA (xfmr)

Springerville	345	Vail		345	1	806 MVA (xfmr)

Winchester	345	Vail		345	1	1858 Amp (CT/relay)

Westwing	345	South		345	1	806 MVA (xfmr)

2008	Saguaro		500	Tortolita		500	1	806 MVA (xfmr)

Saguaro		500	Tortolita		500	2	806 MVA (xfmr)

Springerville	345	Vail		345	1	806 MVA (xfmr)

Winchester	345	Vail		345	1	1858 Amp (CT/relay)

Pinal-West	345	South		345	1	806 MVA (xfmr)

2012	Saguaro		500	Tortolita		500	1	806 MVA (xfmr)

Saguaro		500	Tortolita		500	2	806 MVA (xfmr)

Springerville	345	Vail		345	1	806 MVA (xfmr)

Winchester	345	Vail		345	1	1858 Amp (CT/relay)

Pinal-West	500	Tortolita		500	1	2560 Amp (wire)

Pinal-West	345	South		345	1	806 MVA (xfmr)

Tortolita		345	South		345 	1	806 MVA (xfmr)

SIMULTANEOUS IMPORT LIMIT (SIL)

| Year | SIL MW | MW Losses | Total MW | Critical Outage | Nature of Constraint |
| --- | --- | --- | --- | --- | --- |
| 2005 | 1520 | 89 | 1609 | Cholla – Saguaro 500 kV Line | WECC Voltage Stability Criteria |
| 2008 | 1470 | 74 | 1544 | South T2 345 / 138 kV Xfmr | Irvington / Vail 138kV line loading limit |
| 2012 | 1770 | 116 | 1886 | Springerville – Vail 345 kV Line | Internal Voltage Criterion |

DISCUSSION:

In 2005, the limiting outage for the SIL is the Cholla-Saguaro 500 kV line; at higher loads than the SIL, the WECC voltage stability criteria (QV method) are not met.  All of the fast-switched reactive devices were utilized for this outage.

In 2008, the limiting outage for the SIL is the South 345/138 kV transformer T2; at higher loads than the SIL, the Irvington / Vail 138 kV line is loaded above its rating. The Irvington-Vail lines are budgeted to be upgraded in 2009.  The reason why the SIL is lower in 2008 than in 2005, is that the Pinal West interconnection increases flows on the western side of the transmission system, with more imports through the South T2, making its outage more severe.  If the Irvington-Vail upgrade is moved to 2008, this limitation on the SIL will disappear.

In 2012, the limiting outage for the SIL is the Springerville-Vail 345 kV line; at loads higher than the SIL, the outage solved but did not meet the internal post-outage voltage criterion of .98 per unit. All of the fast-switched reactive devices were utilized for this outage.

There are no known particular external system load or generation patterns that impact the local SIL or RMR conditions.

LOCAL GENERATING UNITS DATA

| Base Loadable | Min Dispatch | Max Dispatch | Qmin | Qmax |
| --- | --- | --- | --- | --- |
| Sundt Unit #1 | 20 MW | 77.5 MW | -15 MVar | 80 Mvar |
| Sundt Unit #2 | 20 MW | 77.5 MW | -15 Mvar | 80 Mvar |
| Sundt Unit #3 | 25 MW | 108.5 MW | -15 Mvar | 65 Mvar |
| Sundt Unit #4 | 35 MW | 118 MW | -30 Mvar | 120 Mvar |
| DMP GT #1* | 40 MW | 73 MW | -15 Mvar | 57 Mvar |
| DMP GT #2 | 40 MW | 73 MW | -15 Mvar | 57 Mvar |
| DMP GT #3 | 40 MW | 73 MW | -15 Mvar | 57 Mvar |

| Peaking | Min Dispatch | Max Dispatch | Qmin | Qmax |
| --- | --- | --- | --- | --- |
| Sundt GT #1 | 22 MW | 22 MW | -10 MVar | 15 MVar |
| Sundt GT #2 | 22 MW | 22 MW | -10 MVar | 15 MVar |
| N. Loop GT #1** | 20 MW | 20 MW | 0 MVar | 0 MVar |
| N. Loop GT #2 | 22 MW | 22 MW | -10 MVar | 15 MVar |
| N. Loop GT #3 | 22 MW | 22 MW | -10 MVar | 15 MVar |
| N. Loop GT #4 | 22 MW | 22 MW | -10 MVar | 15 MVar |

*    DMP GTs are included as dispatchable units as opposed to peaking units because the MVar capacity  combined with location has a significant benefit for voltage stability.

** N. Loop GT #1 is a jet engine with little MVar capacity.

| TEP UNIT MAINTENANCE SCHEDULE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| UPDATED |  |  |  |  |  |  |
| 10/23/2003 |  |  |  |  |  |  |
|  | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 |
| TEP PLANTS |  |  |  |  |  |  |
| H.W. Sundt #1 | 1/15-1/30 | -------- | -------- | 1/12-1/27 | -------- | -------- |
| #2 | -------- | -------- | 3/3-3/18 | -------- | -------- | -------- |
| #3 | -------- | -------- | 2/17-3/4 | -------- | -------- | -------- |
| #4 | -------- | 1/7---2/5 | -------- | -------- | 1/10-2/1 | -------- |
| H.W. Sundt ICT's #1 | 10/2-10/8 | 10/01-10/07 | 9/30-10/06 | 10/05-10/11 | 10/04-10/10 | 10/03-10/09 |
| #2 | 10/9-10/15 | 10/08-10/14 | 10/07-10/13 | 10/12-10/18 | 10/11-10/17 | 10/10-10/16 |
| North Loop ICT's #1 | 10/16-10/22 | 10/15-10/21 | 10/14-10/20 | 10/19-10/25 | 10/18-10/24 | 10/17-10/23 |
| #2 | 10/23-10/29 | 10/22-10/28 | 10/21-10/27 | 10/26-11/01 | 10/25-10/31 | 10/24-10/30 |
| #3 | 10/30-11/05 | 10/29-11/04 | 10/28-11/03 | 11/02-11/08 | 11/01-11/07 | 10/31-11/06 |
| #4 | 11/6-11/12 | 11/05-11/11 | 10/04-10/10 | 11/09-11/15 | 11/08-11/14 | 11/07-11/13 |
| DMP GT | 2/10-2/19 | 2/12-2/18 | 1/28-2/3 | 2/10-0/16 | 2/08-2/14 | 2/07-2/13 |
|  | -------- | -------- | -------- | -------- | -------- | -------- |

PEAK LOAD: ANNUAL RMR CONDITIONS FOR 2005, 2008, 2012

| Year | PEAK MW | MW Losses | Total MW | RMR MW | Critical Outage | Nature of Constraint |
| --- | --- | --- | --- | --- | --- | --- |
| 2005 | 2000 | 110 | 2110 | 178 | South T2 345 / 138 kV Xfmr | Irvington / Vail 138kV line loading limit |
| 2008 | 2121 | 99 | 2220 | 286 | South T2 345 / 138 kV Xfmr | Irvington / Vail 138kV line loading limit |
| 2012 | 2287 | 147 | 2434 | 119 | Tortolita 500/138 Xfmr (#1 or #2) | Remaining Tortolita 500/138 kV Xfmr loading limit |

DISCUSSION:

Many 138kV transmission lines were de-rated by TEP’s Engineering department based on new, more conservative assumptions of temperature and wind speed / direction. Because of this, for 2005 and 2008, generation to relieve thermal overloads becomes as important as MVar availability for RMR conditions.

By the year 2012, all the de-rated 138kV lines needing upgrades will have been upgraded, relieving the thermal constraints on the 138 kV system as long as the less expensive Sundt Units are on line. By 2012 the EHV system will have sufficient new facilities that at peak, it is not voltage stability limited.

Unit commitment with minimum MW required, as well as least cost, was determined for the peak loads of the years studied. Below is a table showing the results. The least MW cost combination of units is shown in this table. Other generator combinations and attendant results are in the Generation Sensitivity Analysis section.  Sundt Units #1 and #2 are equivalent in cost.

| YEAR | Sundt #4 | Sundt #3 | Sundt #2 | Sundt #1 | Sundt #4 MW OUTPUT | Sundt #3 MW OUTPUT | Sundt #2 MW OUTPUT | Sundt #1 MW OUTPUT | TOTAL MW |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2005 | ON | ON |  |  | 118 | 75 |  |  | 193 |
| 2008 | ON | ON |  | ON | 120 | 108.5 |  | 77.5 | 306 |
| 2012 | ON | ON |  |  | 110 | 50 |  |  | 150 |

GENERATION SENSITIVIY ANALYSIS

The effectiveness of the various generating units on relieving RMR conditions is complex for this study, because the de-rating of the 138kV lines has brought thermal overloads more to the forefront; depending on which units are on line, the constraint is either voltage stability or thermal overload, without a large differential in required generation. The difference in results is minimal.

2005 RMR Condition:

The first table is constant MW output with all MW being generated at the Irvington location. The most efficient combination is Sundt Units #3 and #4, which has the lowest loading on Irvington – Vail and also the best results for voltage after the Cholla-Saguaro outage. The least efficient combination is of Sundt Units #1 and #2 with both Irvington gas turbines also on line. The loading on the Irvington-Vail line is slightly higher, and the Cholla-Saguaro outage does not meet the .98 internal voltage criterion.

| Generator #1 | MW | Generator #2 | MW | Generator #3 | MW | Sundt CT MW | Total MW | Irv-Vail loading percent | Cholla-Saguaro 138 volts |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sundt #4 | 118 | Sundt #3 | 75 |  |  |  | 193 | 100.1 | 1.0044 |
| Sundt #4 | 118 | Sundt #1 | 75 |  |  |  | 193 | 100.6 | .9971 |
| Sundt #1 | 70 | Sundt #2 | 70 | Sundt #3 | 53 |  | 193 | 100.6 | .9854 |
| Sundt #3 | 108 | Sundt #1 | 63 |  |  | 22 | 193 | 100.9 | .9892 |
| Sundt #1 | 77 | Sundt #2 | 72 |  |  | 44 | 193 | 101.7 | .9663 |

The second table shows results for the same generated MW output, with MW being produced both at the Irvington location with various combinations of MW generated at DMP and at North Loop with gas turbines. Loading and voltage results vary slightly.

| Generator #1 | MW | Generator #2 | MW | Sundt CT MW | DMP CT MW | NLoop CT MW | Total MW | Irv-Vail loading percent | Cholla-Saguaro 138 volts |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sundt #1 | 75 | Sundt #2 | 74 |  | 44 |  | 193 | 102.2 | .9936 |
| Sundt #1 | 63 | Sundt #3 | 108 |  |  | 22 | 193 | 101.8 | .9938 |
| Sundt #4 | 118 |  |  | 22 | 53 |  | 193 | 101.6 | .9949 |
| Sundt #4 | 118 |  |  |  | 53 | 22 | 193 | 102.6 | .9951 |
| Sundt #3 | 105 |  |  | 44 | 44 |  | 193 | 101.7 | .9988 |

The last table shows results for the same generated MW output, if all MW are from gas turbines. Because the bulk of generation is not in the South end of the system, overloading is worse.

| Sundt CT MW | DMP CT MW | NLoop CT MW | Total MW | Irv-Vail loading percent | Cholla-Saguaro 138 volts |
| --- | --- | --- | --- | --- | --- |
| 44 | 63 | 86 | 193 | 105.6 | .99 |

DISCUSSION:

Generation at Irvington is most effective at relieving the overload on the Irvington-Vail lines, caused by the outage of South T2. Sundt Units #4 and #3 are also best at providing Mvar support for post-outage 138 voltage from loss of Cholla-Saguaro. The gas turbines at North Loop and DMP are effective for providing voltage support for loss of Cholla-Saguaro, but less effective for relieving overloads on Irvington-Vail.

2008 RMR Condition:

The addition of the Pinal West interconnection increases flows on the Western side of the TEP system, decreasing flows from the North and East. Consequently, outage of the Cholla-Saguaro 500kV line decreases in severity, no longer showing up as a constraint in the RMR condition at peak.  The constraint is loading on the Irvington-Vail line following an outage of the South T2.  The most efficient generation for relieving the Irvington-Vail overloads is Sundt #3 and #4, with either Sundt #1 or #2. Some of the slight variation in overloads due to different units’ being on line, is because the auxiliary load of the units are not exactly the same, and some of the generated MW must serve the unit’s own auxiliary load. The Sundt units on the 46 kV system, #1, and #2, are less efficient at relieving Irvington-Vail overloads, but the percentage change is small.

| Generator #1 | MW | Generator #2 | MW | Generator #3 | MW | Sundt CT MW | DMP CT MW | NLoop CT MW | Total MW | Irvington-Vail Loading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sundt #4 | 118 | Sundt #3 | 108.5 | Sundt #1 | 77.5 |  |  |  | 304 | 99.9 |
| Sundt #1 | 77.5 | Sundt #2 | 77.5 | Sundt #3 | 105 | 44 |  |  | 304 | 100.3 |
| Sundt #4 | 118 | Sundt #3 | 108.5 |  |  |  | 73 |  | 299.5 | 102.2 |
| Sundt #2 | 73 | Sundt #2 | 72 |  |  |  | 73 | 86 | 304 | 106.5 |

2012 RMR Condition:

In 2012, there is a similar condition to 2005 in that both voltage and thermal constraints exist, with different generation combinations being more effective for each, but with a narrow variation in results. The first table shows combinations of Sundt steam units, with Units #1 and #2 having less voltage support after a Springerville-Vail outage. The least expensive Sundt Units, #3 and #4, are the most effective for relieving both constraints.

| Generator #1 | MW | Generator #2 | MW | Total MW | Tort xfmr load pct | SP-VL outage |
| --- | --- | --- | --- | --- | --- | --- |
| Sundt #4 | 110 | Sundt #3 | 50 | 160 | 99.6 | 1.0019 |
| Sundt #1 | 77.5 | Sundt #2 | 77.5 | 155 | 99.1 | .9692 |
| Sundt #1 | 77.5 | Sundt #3 | 82.5 | 160 | 98.7 | .9878 |
| Sundt #4 | 110 | Sundt #1 | 50 | 160 | 98.7 | .9989 |

The second table shows that generating the RMR MW at DMP and North Loop only, moves the thermal constraint from Tortolita (the generation is now on the North end of the system) back to Irvington-Vail. Also the lack of the MVar support from Sundt units does not support the post-outage voltage as well for the Springerville-Vail outage, causing it to not meet the internal .98 voltage criterion.

| DMP CT MW | NLoop CT MW | Total MW | Irvington-Vail Loading | SP-VL outage |
| --- | --- | --- | --- | --- |
| 73 | 86 | 159 | 102.3 | .9667 |

MAXIMUM LOAD SERVING CAPACITY (MLSC)

| Year | MLSC MW | MW Losses | Total MW | MW Gen | Critical Outage | Nature of Constraint |
| --- | --- | --- | --- | --- | --- | --- |
| 2005 | 2420 | 131 | 2551 | 552 | South T2 345 / 138 kV Xfmr | Irvington / Vail 138kV line loading limit |
| 2008 | 2445 | 110 | 2555 | 629 | South T2 345 / 138 kV Xfmr | Irvington / Vail 138kV line loading limit |
| 2012 | 2720 | 152 | 2872 | 659 | Tortolita 500/138 Xfmr (#1 or #2) | Remaining Tortolita 500/138 kV Xfmr loading limit |

DISCUSSION:

As with the peak load, the de-rating of the 138kV lines had a significant impact on the ability to import power through the year 2008. Moving the upgrade of the Irvington-Vail lines to 2005 would raise the MLSC for 2005 and 2008.

However, in 2012, the 138kV system does not limit the load serving capacity of the Tucson Control area unless no Irvington steam units are on line. The MLSC is determined by outage of one of the Tortolita 500/138 kV transformers, which loads the remaining transformer. Voltage stability, tested via the WECC Voltage Stability Criteria, is not the limiting factor.

EFFECTIVENESS OF ALTERNATIVE SOLUTIONS

Please refer to jointly-reported CATS study results.

COMPARATIVE ANALYSIS OF ALTERNATIVE SOLUTIONS

It is clear that the upgrading of the de-rated 138kV Irvington-Vail transmission lines, needs to be moved from 2009 to 2005.

As more IPPs continue to go in service, it is theoretically possible that TEP could import all power at peak and generate none locally, if sufficient 138kV transmission line upgrades and sufficient MVar availability could be made available either through SVC or synchronous condenser mode. However, a long-term cost-benefit analysis would have to be done, taking into consideration not only dollars saved on generation but dollars lost in losses and spent for upgrades and MVar support.

Of the combinations of local generating units that provided solutions to the RMR conditions, there is no significant difference in system losses, because the MW import variation is small among the choices, and the flows into the service area are nearly the same.

Summary SIL, MLSC, and Costs for dispatch to mitigate the annual RMR conditions for the years studied:

| Incremental RMR Generation Costs | 2005 | 2008 | 2012 |
| --- | --- | --- | --- |
| SIL | 1600 | 1550 | 1850 |
| MLSC | 2500 | 2525 | 2800 |
| Peak Load | 2000 | 2121 | 2286 |
| RMR | 348 | 826 | 385 |
| Annual Total | $ 68,061 | $ 307,179 | $ 301,885 |

Total emission pollutants produced by the lowest local generation dispatch mitigating the annual RMR condition, for the years studied:

Environmental Summary

Annual pollutants are based on estimated RMR output as defined by the ACC data request, and not the incremental difference between the possible market alternative.

| 2005 RMR Environmental Output | Estimated SO2 | Estimated NOx | Estimated PM | Estimated CO |
| --- | --- | --- | --- | --- |
| Sundt Steam Gas (lbs) | 30 | 7,679 | 230 | 901 |
| 2008 RMR Environmental Output | Estimated SO2 | Estimated NOx | Estimated PM | Estimated CO |
| Sundt Steam Gas (lbs) | 185 | 48,042 | 1,441 | 5,639 |
| DeMoss Petrie Gas Turbine (lbs) | 3 | 168 | 63 | 158 |
| Sundt Gas Turbine (lbs) | 0 | 11 | 4 | 10 |
| 2012 RMR Environmental Output | Estimated SO2 | Estimated NOx | Estimated PM | Estimated CO |
| Sundt Steam Gas (lbs) | 21 | 5,415 | 162 | 636 |